## 2024 IECC
| HEALTH CARE CLINIC SOO, IECC 2024 | [36 empty] | version 1.4
SEQUENCE OF OPERATIONS
REFERENCE SPECIFICATION SECTION/S: [SECTION #]
REFERENCE DRAWING/S: [DRAWING #]
PROJECT OPERATING SCHEDULE: OPEN = [TIME]; CLOSE = [TIME]
| PROJECT PARAMETERS |  |  | OCCUPANT SENSOR (SUPERSEDES TIME-SWITCH AND DAYLIGHT) | [7 empty] | TIME-SWITCH (SUPERSEDES DAYLIGHT ONLY) | [5 empty] | DAYLIGHT RESPONSE (SUPERSEDES NONE) |  | MANUAL CONTROL (SUPERSEDES ALL) |  |  |  | ADDITIONAL SETTINGS | [8 empty] | INTEGRATION |  |  |  |  | NOTES AND REFERENCES
| CONNECTIVITY |  | LOAD TYPE(S) | TYPE | TURN ON |  | REDUCE / TURN OFF |  |  | NARRATIVE |  | TURN ON |  | REDUCE / TURN OFF |  | NARRATIVE |  | DIMMING |  | DEVICE |  | ADDITIONAL LIGHTING CONTROLS |  | SETPOINT (ADJ) |  | FADE RATE SECONDS (ADJ) |  |  | COLOR CONTROL |  | LIMITS |  | AUTOMATIC RECEPTACLE CONTROL | COMMUNICATION
| STANDALONE / NETWORKED | WIRED / WIRELESS | CONTINUOUS DIMMING / NON-DIM | DUAL-TECH / PIR / ULTRASONIC | AUTO / MANUAL | LEVEL | TIMEOUT (ADJ) | AUTO / MANUAL | LEVEL | TURN ON | REDUCE / TURN OFF | TIME (ADJ) | LEVEL | TIME (ADJ) | MANUAL OVERRIDE TIMEOUT (ADJ) | TURN ON | REDUCE / TURN OFF | CONTINUOUS / STEP / NON-DIM | SETPOINT (ADJ) | MANUAL ON/OFF + SCENES | RAISE & LOWER | COLOR CONTROL | ON/OFF FOR SUPPLEMENTAL LIGHTING | ADR | EMERGENCY LIGHT LEVEL (UL924) | ON | OFF | ADR | COLOR TUNING | TUNABLE WHITE | HIGH-END TRIM (ADJ) | LOW-END TRIM (ADJ) | OCCUPANT SENSOR / TIME-SWITCH | BUILDING MANAGEMENT (BMS) | WINDOW TREATMENT | FIRE ALARM | AUDIO/VIDEO
SPACE TYPE
Patient Room | [9 empty] | Space is exempt from automatic controls. | Space is exempt from automatic controls. | [9 empty] | FALSE |  | TRUE |  | 100%
Nursing Station |  |  | continuous dimming | [17 empty] | TRUE |  | TRUE |  | 100%
Imaging Room |  |  | continuous dimming | [17 empty] | TRUE |  | TRUE |  | 100% | 5 | 5
Stairwell | [9 empty] | Lighting will remain On at 100% in interior exit stairways | [10 empty] | FALSE |  | FALSE |  | 100%
Restroom |  |  |  |  | auto | 100% | 20 min | auto | 0% | Upon occupancy within a control zone, lighting in that zone will automatically turn On to Level. | Upon all occupants leaving a control zone, after Timeout, lighting in that zone will automatically go to Reduce/Turn Off. | [6 empty] | continuous | [ADD] fc |  | FALSE |  | FALSE |  | 100%
Mother's Wellness |  |  |  |  | auto | 100% |  | auto | 0% | [11 empty] | FALSE |  | FALSE |  | 100%
Lobby |  |  | continuous dimming |  | auto | 100% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | TRUE |  | TRUE |  | 100% | 5 | 5
Interior Parking Areas |  |  |  |  | auto | 100% |  | auto | 70% |  |  | open | 100% | close |  | Turn lighting On at scheduled Time to Level. | Turn lighting Off at scheduled Time. | step | [ADD] fc |  | FALSE |  | FALSE |  | 100%
Corridor |  |  |  |  | auto | 100% |  | auto | 50% |  |  | open | 100% | close | 2 hours | Turn lighting On at scheduled Time to Level. | Turn lighting Off at scheduled Time and when space is unoccupied. Keep the lights on for Manual Override Timeout when activated by manual overide controls. | continuous | [ADD] fc |  | FALSE |  | FALSE |  | 100%
Locker Room |  |  |  |  | auto | 100% |  | auto | 0% | [11 empty] | FALSE |  | FALSE |  | 100%
Exam Room |  |  | continuous dimming |  | auto | 50% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | TRUE |  | TRUE |  | 100% | 5 | 5 | [5 empty] | occupant sensor
Medical Supply Room |  |  |  |  | auto | 50% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | FALSE |  | FALSE |  | 100%
Lounge / Breakroom |  |  | continuous dimming |  | auto | 50% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | TRUE |  | TRUE |  | 100% | 5 | 5 | [5 empty] | occupant sensor
Enclosed Offices |  |  |  |  | auto | 50% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | FALSE |  | TRUE |  | 100% | [7 empty] | occupant sensor
Conference/Meeting Room |  |  | continuous dimming |  | auto | 50% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | TRUE |  | TRUE |  | 100% | 5 | 5 | [5 empty] | occupant sensor
Waiting Room |  |  |  |  | manual | 100% |  | auto | 0% | Lighting is turned On to Level manually from manual control device. | [7 empty] | continuous | [ADD] fc |  | FALSE |  | TRUE |  | 100%
Telemedicine Room |  |  |  |  | manual | 100% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | FALSE |  | TRUE |  | 100%
Janitor Closet |  |  |  |  | manual | 100% |  | auto | 0% | [11 empty] | FALSE |  | FALSE |  | 100%
Electrical/Mech/Equip Room |  |  |  |  | manual | 100% |  | auto | 0% | [11 empty] | FALSE |  | FALSE |  | 100%
Storage Room |  |  |  |  | manual | 50% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | FALSE |  | FALSE |  | 100%
Pharmacy |  |  |  |  | manual | 100% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | FALSE |  | TRUE |  | 100%
Other Spaces (≤ 300 sq ft) |  |  |  |  | manual | 100% |  | auto | 0% | [8 empty] | continuous | [ADD] fc |  | FALSE |  | TRUE |  | 100%
ADDITIONAL SCOPE FOUND HERE!

## Description
Produced by the Lighting Controls Academy, a NEMA coalition, this Control Intent Narrative/Sequence of Operations (CIN/SOO) template includes minimum requirements from the 2024 IECC. It is intended for educational use and may be modified and used at the user’s own risk. For official code interpretation, consult the Authority Having Jurisdiction (AHJ).
A CIN outlines space types and general control requirements, while an SOO defines specific system triggers and behaviors. Together, they provide a shared reference to improve project coordination and control quality.
Users can customize the template by adjusting parameters and entering project-specific data. Remove columns that are not needed or have no information. Use drop-downs with sample inputs, noting red “ADD” fields prompt user input. Additional columns address design elements beyond code, such as integration. A notes column supports references and extra details. The layout is optimized for print on an ANSI E (34x44) sized sheet, but can be modified for smaller sheets. Please test print prior to use on a smaller sheet size.

## Disclaimer
This Control Intent Narrative/Sequence of Operations template is based on minimum requirements from the 2024 International Energy Conservation Code. It is intended for educational use only. Users may adapt it at their own risk and should consult the Authority Having Jurisdiction (AHJ) for final code interpretation.
The content is based on sources believed to be reliable. The Lighting Controls Academy, NEMA, and their employees, vendors, and members are not liable for any errors, omissions, or misuse of this information.
This material is for informational purposes and is not a substitute for professional design, engineering, or consulting services. Such services should be provided by qualified, licensed professionals.